## Sheet1
Ref No.
Date
Client
Location
Contact
Q | Ventilation flow rate
Qcp | Generation rate of CO2
C | Indoor CO2 concentration
Cs | Outdoor CO2 concentration
Ci | Initial CO2 concentration in the room
n | Air change rate
V | Room volume
t | Time
Occupancy | Qcp | V | Ci
Nos | m3/s | m3 | ppm / 1000000
36 | 0.00018 | 383 | 0.00058
Q = Qcp / (C - Cs)
Qcp | C | Cs | Q | Q
m3/s | ppm / 1000000 | ppm / 1000000 | m3/s | cfm
0.00018 | 0.001 | 0.00037 | 0.28571 | 605.042
C = {Cs + (Qcp / Q)} * {1 - (e^ -nt)} + {Ci (e^-nt)}
Q | Qcp | Cs | Ci | V | n | t | Cs+(Qcp/Q) | 1-(e^-nt) | Ci(e^-nt) | C | C | t
m3/s | m3/s | ppm / 1000000 | ppm / 1000000 | m3 | 1/s | s |  |  |  | ppm / 1000000 | ppm | min
0.28571 | 0.00018 | 0.00037 | 0.00058 | 383 | 0.00074599 | 0 | 0.001 | 0 | 0.00058 | 0.00058 | 580 | 0
0.28571 | 0.00018 | 0.00037 | 0.00058 | 383 | 0.00074599 | 500 | 0.001 | 0.31133 | 0.00039943 | 0.00071076 | 710.7592 | 8.3333
0.28571 | 0.00018 | 0.00037 | 0.00058 | 383 | 0.00074599 | 1000 | 0.001 | 0.52574 | 0.00027507 | 0.00080081 | 800.809 | 16.6667
0.28571 | 0.00018 | 0.00037 | 0.00058 | 383 | 0.00074599 | 2000 | 0.001 | 0.77507 | 0.00013046 | 0.00090553 | 905.5308 | 33.3333
0.28571 | 0.00018 | 0.00037 | 0.00058 | 383 | 0.00074599 | 4000 | 0.001 | 0.94941 | 2.9343e-05 | 0.00097875 | 978.7513 | 66.6667
0.28571 | 0.00018 | 0.00037 | 0.00058 | 383 | 0.00074599 | 6000 | 0.001 | 0.98862 | 6.6001e-06 | 0.00099522 | 995.2206 | 100
0.28571 | 0.00018 | 0.00037 | 0.00058 | 383 | 0.00074599 | 10000 | 0.001 | 0.99942 | 3.3391e-07 | 0.00099976 | 999.7582 | 166.6667
0.28571 | 0.00018 | 0.00037 | 0.00058 | 383 | 0.00074599 | 12000 | 0.001 | 0.99987 | 7.5106e-08 | 0.00099995 | 999.9456 | 200
0.21429 | 0.00018 | 0.00037 | 0.00058 | 383 | 0.00055949 | 0 | 0.00121 | 0 | 0.00058 | 0.00058 | 580 | 0
0.21429 | 0.00018 | 0.00037 | 0.00058 | 383 | 0.00055949 | 500 | 0.00121 | 0.24402 | 0.00043847 | 0.00073374 | 733.7355 | 8.3333
0.21429 | 0.00018 | 0.00037 | 0.00058 | 383 | 0.00055949 | 1000 | 0.00121 | 0.4285 | 0.00033147 | 0.00084996 | 849.9557 | 16.6667
0.21429 | 0.00018 | 0.00037 | 0.00058 | 383 | 0.00055949 | 2000 | 0.00121 | 0.67339 | 0.00018943 | 0.0010042 | 1004.2351 | 33.3333
0.21429 | 0.00018 | 0.00037 | 0.00058 | 383 | 0.00055949 | 4000 | 0.00121 | 0.89333 | 6.1871e-05 | 0.0011428 | 1142.7949 | 66.6667
0.21429 | 0.00018 | 0.00037 | 0.00058 | 383 | 0.00055949 | 6000 | 0.00121 | 0.96516 | 2.0208e-05 | 0.0011881 | 1188.0501 | 100
0.21429 | 0.00018 | 0.00037 | 0.00058 | 383 | 0.00055949 | 10000 | 0.00121 | 0.99628 | 2.1557e-06 | 0.0012077 | 1207.6585 | 166.6667
0.21429 | 0.00018 | 0.00037 | 0.00058 | 383 | 0.00055949 | 12000 | 0.00121 | 0.99879 | 7.0406e-07 | 0.0012092 | 1209.2352 | 200
0.35714 | 0.00018 | 0.00037 | 0.00058 | 383 | 0.00093249 | 0 | 0.000874 | 0 | 0.00058 | 0.00058 | 580 | 0
0.35714 | 0.00018 | 0.00037 | 0.00058 | 383 | 0.00093249 | 500 | 0.000874 | 0.37265 | 0.00036387 | 0.00068956 | 689.5579 | 8.3333
0.35714 | 0.00018 | 0.00037 | 0.00058 | 383 | 0.00093249 | 1000 | 0.000874 | 0.60643 | 0.00022827 | 0.00075829 | 758.2894 | 16.6667
0.35714 | 0.00018 | 0.00037 | 0.00058 | 383 | 0.00093249 | 2000 | 0.000874 | 0.8451 | 8.9842e-05 | 0.00082846 | 828.4594 | 33.3333
0.35714 | 0.00018 | 0.00037 | 0.00058 | 383 | 0.00093249 | 4000 | 0.000874 | 0.97601 | 1.3917e-05 | 0.00086695 | 866.9458 | 66.6667
0.35714 | 0.00018 | 0.00037 | 0.00058 | 383 | 0.00093249 | 6000 | 0.000874 | 0.99628 | 2.1557e-06 | 0.00087291 | 872.9073 | 100
0.35714 | 0.00018 | 0.00037 | 0.00058 | 383 | 0.00093249 | 10000 | 0.000874 | 0.99991 | 5.1723e-08 | 0.00087397 | 873.9738 | 166.6667
0.35714 | 0.00018 | 0.00037 | 0.00058 | 383 | 0.00093249 | 12000 | 0.000874 | 0.99999 | 8.0119e-09 | 0.000874 | 873.9959 | 200
C = (Qcp / Q) + Cs
Q | Qcp | Cs | C | C | Q
m3/s | m3/s | ppm / 1000000 | ppm / 1000000 | ppm | cfm
0.14286 | 0.00018 | 0.00037 | 0.00163 | 1630 | 302.521
0.21429 | 0.00018 | 0.00037 | 0.00121 | 1210 | 453.7815
0.28571 | 0.00018 | 0.00037 | 0.001 | 1000 | 605.042
0.35714 | 0.00018 | 0.00037 | 0.000874 | 874 | 756.3025
0.42857 | 0.00018 | 0.00037 | 0.00079 | 790 | 907.563